LAITRAM ELECTRIC SYSTEM REDUNDANCY Dual Source Automatic Transfer & Generator Backup Formal Sequence of Operation

| Document Type | Sequence of Operation / Customer Presentation |
| --- | --- |
| System | Dual 3000 kVA Pad-Mount Transformers (A & B) with Single Generator |
| Voltage | Utility 13.8 kV → 480 V, 3Ø, Secondary Gear |
| Revision | Rev A — For Customer Review |
| Date | August 12, 2026 |

This document describes the proposed modification to the existing dual-transformer secondary distribution system to provide automatic open-transition transfer between Sources A and B upon loss of either secondary source, automatic closed-transition retransfer when the preferred source returns, and delayed generator transfer only if alternate-source transfer is unsuccessful. It is intended for formal customer review of capabilities, limitations, timing criteria, and open decision items.

PURPOSE OF THIS DOCUMENT Present a clear, formal Sequence of Operation (SOO) so the customer fully understands how the modified system will behave under utility loss, phase loss, successful and unsuccessful alternate-source transfer, generator start/transfer, and closed-transition retransfer — including utility coordination, fault-duty considerations, and items requiring customer input before final design.

1. EXISTING SYSTEM SUMMARY

The facility is served by two utility-fed pad-mounted transformers. Each customer service is approximately 3000 kVA, 13.8 kV primary to 480 V three-phase secondary, with a fused disconnect on the primary side. Secondary electrical gear is provided on each transformer and presently includes automatic transfer to a single standby generator on power loss, with closed-transition retransfer capability. Because there is only one generator, operator selection determines which transformer’s loads are protected by the generator. A manually operated secondary tie breaker allows loads to be transferred between transformers, including manual closed-transition retransfer.

1.1 Existing Configuration (As Understood)

| Source A | Utility → 3000 kVA pad-mount XFMR A (13.8 kV / 480 V, 3Ø) → fused disconnect → secondary gear A |
| --- | --- |
| Source B | Utility → 3000 kVA pad-mount XFMR B (13.8 kV / 480 V, 3Ø) → fused disconnect → secondary gear B |
| Generator | Single standby generator; selectable protection of either A or B load group |
| ATS / Controls | Per-transformer automatic transfer to generator on power loss; closed-transition retransfer |
| Tie Breaker | Secondary-side tie between A and B; presently manual transfer / manual closed-transition retransfer |
| Gear Fault Rating | 100 kA rated fault current (as stated) |

2. PROPOSED OBJECTIVES

The requested modifications establish the following hierarchy of protection:

| Priority | Action | Transition Type |
| --- | --- | --- |
| 1 — Primary | On loss of A or B secondary source, automatically transfer loads to the alternate healthy transformer via the tie. | Open transition |
| 1a — Retransfer | When the failed utility/source returns and is stable, automatically retransfer to the preferred / restored source. | Closed transition |
| 2 — Secondary | If alternate-source transfer fails or the alternate source is also unavailable, start and transfer to the generator (after intentional delay). | Per existing ATS practice |

In short: transformer-to-transformer redundancy becomes the first line of defense; generator backup remains available but is intentionally delayed so it does not race the alternate-source transfer.

3. DEFINITIONS & OPERATING MODES

• Preferred Source: The normally assigned utility/transformer source for a given load group (A or B). Final preferred-source designation to be confirmed with the customer.

• Alternate Source: The other utility/transformer source, made available through the secondary tie breaker.

• Open Transition: Break-before-make. Loads briefly go dark (or ride through on UPS/process inertia if present) while one source opens before the other closes.

• Closed Transition: Make-before-break for a controlled, short paralleling interval. Used for automatic retransfer (and existing generator retransfer) subject to sync/utility approval.

• Source Failure: Sustained undervoltage, loss of phase, severe phase imbalance, or other defined abnormal voltage condition lasting beyond the failure timer.

• Source Available / Healthy: Voltage within acceptable band on all phases, correct phase rotation, and stable for the defined availability timer.

4. POWER LOSS & PHASE LOSS DETECTION CRITERIA

Reliable detection is essential to avoid nuisance transfers while still protecting loads from damaging single-phasing and deep undervoltage. The following criteria are recommended as the design basis and will be finalized during detailed engineering with the selected relay/ATS/controller manufacturer.

4.1 Recommended Undervoltage / Phase-Loss Setpoints (Design Basis)

| Parameter | Recommended Design Basis | Notes |
| --- | --- | --- |
| Nominal voltage | 480 V, 3Ø | Secondary sensing preferred |
| Undervoltage pickup (source fail) | Typically 80–85% of nominal (≈384–408 V) | Any phase; adjustable |
| Severe undervoltage / total loss | Typically <70% of nominal | Accelerated fail path optional |
| Phase loss / single-phasing | Loss of one or more phases, or phase voltage imbalance typically >15–20% | Must transfer even if remaining phases look “OK” |
| Overvoltage inhibit (optional) | Typically >110–115% of nominal | Block transfer onto unhealthy alternate |
| Phase rotation / sequence | Correct ABC (or site standard) | Inhibit close if reverse rotation |
| Frequency (for gen / sync) | Within ±0.5 Hz (or manufacturer sync window) for closed transition | Required for closed-transition retransfer |

IMPORTANT — SINGLE-PHASING Phase-loss / voltage-imbalance detection is mandatory. Relying only on an average three-phase voltage or a single phase-to-phase measurement can leave motors and process equipment energized on a damaged feed. Sensing shall monitor all three phases on each secondary source.

4.2 Sensing Location

• Primary sensing: 480 V secondary bus or ATS/source-side PTs on Transformer A gear and Transformer B gear.

• Optional supervisory: status of primary fused disconnects / transformer alarms if available (does not replace secondary voltage sensing).

• Tie and breaker position feedback (52a/52b or equivalent) required for interlocking and sequence logic.

5. RECOMMENDED TIMING SUMMARY

The following timers form the proposed customer-facing design basis. Exact values will be coordinated with utility requirements, process ride-through needs, existing ATS settings, and manufacturer recommendations.

| Timer / Event | Recommended Delay | Typical Range | Intent |
| --- | --- | --- | --- |
| Source Failure confirmation (Tfail) | 1.0–1.5 seconds | 0.5–3 s | Confirm sustained loss / phase loss; avoid nuisance on momentary dips |
| Open-transition alternate-source transfer initiate | Immediately after Tfail + interlocks OK | — | Open failed source breaker, close tie (or close alternate path) per interlocking |
| Dead-bus / transfer open time | As short as gear allows (typically <1–2 s total) | Gear-dependent | Minimize outage during A↔B open transition |
| Alternate source “available” proof (Tavail) | 1–3 seconds stable | 1–5 s | Do not close onto unstable alternate |
| Generator start delay (Tgen-delay) | 5–10 seconds after source fail | 5–15 s | Allow A↔B transfer to complete first; start gen only if alternate transfer unsuccessful or alternate also failed |
| Generator transfer (existing ATS) | Per existing ATS (after gen ready / warm-up) | As installed | Only if primary alternate-source path did not restore power |
| Utility / preferred source return stability (Tretrans-wait) | 5–10 minutes | 1–30 min (utility/process dependent) | Confirm restored source is stable before closed-transition retransfer |
| Closed-transition paralleling window | 100 ms typical (≤100–150 ms common) | Per utility / sync check relay | Limit intentional paralleling duration |

Proposed customer presentation defaults (subject to final coordination): Tfail = 1.5 s; Tgen-delay = 8 s; Tretrans-wait = 5 minutes; closed-transition paralleling ≤ 100 ms.

6. FORMAL SEQUENCE OF OPERATION

6.1 Normal Operation

1. Transformer A secondary breaker closed; Transformer B secondary breaker closed; Tie breaker open (sources isolated).

2. Each load group is served by its respective transformer. Generator is in standby (not paralleled / not serving load), with the existing selector determining which load group the generator protects.

3. Protective relays / controllers continuously monitor three-phase voltage, phase rotation, and breaker status on Sources A and B.

4. Manual operations (maintenance transfer via tie, generator test, etc.) remain available under supervised control, subject to interlocking.

6.2 Loss of Source A (Source B Healthy) — Primary Path: Auto Open-Transition to B

1. Detect: Source A voltage falls below undervoltage / phase-loss criteria.

2. Confirm: Source Failure timer (Tfail ≈ 1.0–1.5 s) times out, confirming a sustained abnormal condition (not a momentary dip).

3. Qualify alternate: Controller verifies Source B is healthy (voltage, phases, rotation within limits for Tavail) and that no inhibiting fault lockout, maintenance mode, or interlocking condition is active.

4. Transfer: Open transition sequence:

– Open Source A secondary main (or isolate failed source path as designed).

– Confirm A is open (breaker feedback).

– Close Tie breaker to pick up A loads from Source B (or execute the engineered open-transition path that places A loads on B).

5. Result: A loads are now served from Transformer B through the tie. Total intentional dead time is minimized consistent with open-transition interlocking.

6. Generator: Generator start remains inhibited or is cancelled if A↔B transfer is successful and load voltage is restored before Tgen-delay expires. If generator already received a start signal, it returns to cooldown/standby per existing logic.

7. Hold: System remains on single-transformer supply until Source A returns and retransfer conditions are met (Section 6.5).

6.3 Loss of Source B (Source A Healthy) — Mirror Sequence

The sequence is identical with A and B roles reversed: confirm failure of B, verify A healthy, open-transition transfer B loads onto A via the tie, suppress/cancel generator transfer if successful, and hold until closed-transition retransfer.

6.4 Unsuccessful Alternate-Source Transfer or Dual-Source Loss — Generator Path

1. If Source A fails and Source B is also unhealthy, or if tie/alternate close is blocked (fault lockout, breaker failure, interlocking, overload inhibit, etc.), the alternate-source path is declared unsuccessful.

2. After Generator Start Delay (Tgen-delay ≈ 5–10 s from initial source fail — long enough for a successful A↔B transfer to complete and be proven), the generator receives a start command for the selected protected load group.

3. When the generator is ready (voltage/frequency in band), the existing ATS transfers the selected loads to the generator per the present open-transition (or as-installed) generator transfer sequence.

4. Closed-transition retransfer from generator back to utility remains per the existing system once utility is restored and stable — coordinated so it does not conflict with the new A↔B retransfer logic.

5. If only one source failed but alternate transfer failed, operator alarm/annunciation shall clearly indicate “Alternate Source Transfer Fail — Generator Active (or Generator Starting).”

GENERATOR SELECTIVITY LIMITATION Because only one generator exists, simultaneous loss of both A and B (or failure of alternate transfer while the generator selector is assigned to only one side) means the non-selected load group may remain without generator backup. Customer must understand and accept this limitation, or consider future generator capacity / dual-ATS strategy.

6.5 Return of Failed Utility Source — Automatic Closed-Transition Retransfer

1. Detect return: Failed source voltage returns within healthy band on all phases with correct rotation.

2. Stability wait: Source Return Stability timer (Tretrans-wait ≈ 5–10 minutes) must expire with continuous healthy voltage. This reduces risk of retransfer onto a flickering or unstable utility restoration.

3. Sync check: Sync-check / paralleling permissive verifies voltage difference, phase angle, and frequency within closed-transition window (and any utility-mandated limits).

4. Retransfer: Closed-transition retransfer:

– Close the restored source breaker (brief parallel of A and B through the tie / mains as engineered).

– Within the allowed paralleling window (typically ≤100 ms), open the tie (or open the alternate main, per the designed breaker pair) to separate sources.

– Confirm breaker positions and return to Normal Operation.

5. Fail-safe:If sync conditions cannot be met within a retry window, the system shall either (a) alarm and remain on alternate source for manual/supervised retransfer, or (b) fall back to a supervised open-transition retransfer — customer preference to be confirmed.

6.6 Manual Operations (Retained / Enhanced)

• Manual open- or closed-transition transfer via HMI/selector remains available for maintenance, subject to interlocking and sync check.

• Existing manual tie operations should be integrated into the same interlocking scheme so automatic and manual modes cannot conflict.

• A Lockout / Maintenance mode shall block automatic A↔B transfer and automatic retransfer while allowing safe manual control.

7. INTERLOCKING, PROTECTION & FAULT CONSIDERATIONS

7.1 Minimum Interlocks

• Prevent paralleling of A and B except during intentional, timed closed-transition retransfer under sync-check permissive.

• Block tie close if either source is faulted / lockout relay operated (50/51, 50G/51G, differential, arc-flash, etc., as applicable).

• Breaker failure / disagreement alarm if commanded open/close is not confirmed within time.

• Inhibit automatic transfer into a source that is undervoltage, reverse rotation, or under active protective lockout.

• Coordinate generator ATS and A↔B controller so both do not attempt conflicting transfers.

• Optional load-shed or capacity check before placing both load groups on one transformer (see Section 8).

7.2 Fault Interrupting Rating & Closed-Transition Risk

The secondary gear is stated as 100 kA fault-current rated. Closed-transition retransfer intentionally parallels Sources A and B for a short interval. During that interval, available fault current at the paralleled bus can approach the arithmetic (or more accurately, vector) sum of contributions from both utility transformers — potentially exceeding the fault duty seen in normal isolated operation.

• Before enabling automatic closed-transition retransfer, a short-circuit study must confirm that available fault current during the paralleling window does not exceed the 100 kA rating of breakers, buses, and protective devices — with appropriate margins and X/R considerations.

• If paralleled fault duty exceeds equipment ratings, closed-transition automatic retransfer shall not be enabled until mitigations are implemented (e.g., utility reactor/impedance confirmation, faster paralleling window with proven clearing coordination, equipment upgrade, or open-transition retransfer only).

• Protective device settings must be reviewed so that a fault occurring during the brief parallel does not cascade into unnecessary dual-source outages or exceed interrupting ratings.

• Arc-flash incident energy may change under paralleled conditions; labels and PPE categories should be reviewed after the study.

HOLD POINT — FAULT DUTY Automatic closed-transition retransfer shall remain disabled (or limited to supervised manual operation) until the short-circuit / equipment duty evaluation is completed and accepted. Stated 100 kA gear rating is necessary but not sufficient without verifying paralleled available fault current.

8. CAPABILITIES & LIMITATIONS (CUSTOMER UNDERSTANDING)

8.1 Capabilities After Modification

• Automatic restoration of loads to the alternate transformer on loss of A or B, without waiting for generator start — typically restoring power in a few seconds via open transition.

• Automatic closed-transition return to the restored preferred source after a stability delay, minimizing a second outage on retransfer (subject to utility approval and fault-duty clearance).

• Generator remains as secondary backup, delayed so it does not race a successful A↔B transfer.

• Clearer hierarchy: Utility alternate first, generator second.

• Retention of manual transfer / maintenance modes under common interlocking.

8.2 Limitations & Issues the Customer Must Accept / Decide

• Momentary outage: Open-transition A↔B transfer causes a brief power interruption. Sensitive loads need UPS, ride-through, or process sequencing. This is not a no-break transfer between transformers on failure.

• Single generator: Only one generator. Non-selected loads are not generator-protected. Dual utility loss or failed alternate transfer still leaves a coverage gap on the non-selected side.

• Transformer capacity: Serving both load groups from one 3000 kVA transformer may overload that transformer depending on coincident demand. Automatic transfer may require load shed, demand limits, or operator procedures.

• Utility approval: Closed-transition retransfer requires utility interconnection / paralleling approval and sync-check compliance. Without approval, retransfer must remain open-transition or manual-only.

• Fault duty: Paralleled fault current may challenge the 100 kA rating; study required before auto closed retransfer.

• Common-mode utility failure: If the utility event is upstream and common to both services, A↔B transfer provides no benefit; generator is the only backup for the selected loads.

• Fault vs. source loss: Primary fused-disconnect / transformer faults, cable faults on the secondary, or bus faults may require lockout that blocks automatic tie close — correctly so, to avoid closing into a fault.

• Controls integration: Logic complexity increases (A↔B controller + existing generator ATS). Commissioning, periodic testing, and operator training are required.

9. UTILITY APPROVAL FOR CLOSED-SOURCE RETRANSFERS

Closed-transition retransfer creates a momentary parallel between two utility-derived sources (through customer secondary gear). Most utilities treat this as a paralleling / closed-transition operation requiring formal review.

• Obtain written utility approval (or interconnection amendment) for automatic closed-transition retransfer between the two services, including maximum paralleling time and sync-check requirements.

• Confirm whether the two 13.8 kV feeds are from the same feeder/bus or diverse sources — this affects both reliability benefit and paralleling risk.

• Confirm utility requirements for anti-islanding, reverse power, and any telemetry/notification during automatic operations.

• Align generator closed-transition retransfer approvals (if already granted) with the new A↔B closed-transition scheme so settings and responsibilities are consistent.

• If approval is denied or delayed, the design can proceed with automatic open-transition A↔B transfer and open-transition (or manual closed) retransfer — with the customer informed of the second brief outage on return.

10. PROPOSED DEFAULT SETTINGS (FOR DISCUSSION)

| Setting | Proposed Default for Customer Presentation |
| --- | --- |
| Undervoltage / source fail pickup | 85% of 480 V (≈408 V), any phase; imbalance >20% = phase loss |
| Source failure confirmation (Tfail) | 1.5 seconds |
| Generator start delay (Tgen-delay) | 8 seconds from source fail (cancel if A↔B transfer proven) |
| Return-to-source stability (Tretrans-wait) | 5 minutes continuous healthy voltage |
| Closed-transition max parallel time | 100 milliseconds (sync-check permissive required) |
| Retransfer if sync not achieved | Alarm + remain on alternate; manual/supervised retransfer |

These defaults are engineering recommendations for presentation and negotiation — not final commissioned settings until load study, utility review, and manufacturer coordination are complete.

11. QUESTIONS FOR THE CLIENT

The following questions should be resolved (or formally deferred with assumptions) before detailed design and procurement:

11.1 Load & Capacity

1. What is the measured / design coincident demand on Transformer A and Transformer B (kVA or amps)?

2. If one transformer must carry both load groups, what is the expected peak, and for how long is that acceptable?

3. Is automatic load shedding required/desired before tie close when one source is lost? If so, which loads and in what order?

4. Are there UPS, VFD, or process systems that cannot tolerate the open-transition dead time? What ride-through duration do they need?

11.2 Preferred Operating Philosophy

5. Should each side always prefer its “home” transformer, or is there a designated primary transformer?

6. On return of the failed source, do you want fully automatic closed-transition retransfer, or operator-initiated closed-transition after alarm?

7. If sync-check fails, do you prefer to stay on the alternate source indefinitely until manual action, or allow automatic open-transition retransfer after an additional delay?

8. Should automatic A↔B transfer be enabled at all times, or only in certain operating modes / shifts?

11.3 Generator Strategy

9. Which loads / which transformer side must the generator protect today, and is that selection changed seasonally or by production?

10. Is an 8-second generator start delay acceptable relative to process/UPS needs if A↔B transfer fails?

11. Should the generator start in parallel with the A↔B attempt (start early, transfer only if needed), or strictly after A↔B failure is proven?

12. Is there a future plan for a second generator or a generator large enough to cover both sides?

11.4 Utility & Site Electrical

13. Are the two 13.8 kV services from independent utility feeders/substations, or the same upstream source?

14. Has the utility previously approved closed-transition paralleling for the generator retransfer? Can that approval be extended to A↔B retransfer?

15. Who is the utility interconnection contact, and what is the expected review path/timeline for closed-transition approval?

16. Are there existing sync-check relays, and what are their present settings / paralleling time limits?

11.5 Protection, Gear & Studies

17. Can you provide one-line diagrams, breaker/ATS cut sheets, and the short-circuit study used to establish the 100 kA rating?

18. What are the existing main and tie breaker models, continuous ratings, and interrupting ratings (and bus bracing)?

19. Are there known downstream fault history, arc-flash labels, or coordination study constraints we must preserve?

20. Is there a preference for a dedicated automatic transfer controller / PLC vs. manufacturer ATS/logic packages?

11.6 Operations & Maintenance

21. Who will operate and maintain the system, and what training/documentation is required at turnover?

22. What annunciation is required (local HMI, building BMS, email/SMS, SCADA)?

23. How often should automatic transfer / retransfer be functionally tested without disrupting production?

24. Are there lockout/tagout or production constraints that require a Maintenance mode inhibiting auto transfer?

12. RECOMMENDED NEXT STEPS

1. Customer review of this Sequence of Operation and written responses to Section 11 questions.

2. Confirm utility closed-transition approval path and feeder diversity.

3. Obtain one-lines, load data, and short-circuit / coordination documentation; perform paralleled fault-duty check against 100 kA gear.

4. Finalize timers, setpoints, and fail-safe retransfer philosophy.

5. Detailed design: interlocking, controls integration with existing generator ATS, HMI/alarms, and bill of materials.

6. Factory / site acceptance testing script covering A fail, B fail, dual fail, failed tie close, return/retransfer, and maintenance mode.

DOCUMENT STATUS Rev A — Conceptual / presentation Sequence of Operation for customer discussion. Not a construction specification. Final settings, interlocking diagrams, and utility-approved paralleling limits will supersede this document after detailed engineering.

13. ACKNOWLEDGMENT (OPTIONAL)

By signing below, the customer acknowledges receipt and review of this Sequence of Operation, including the stated capabilities, limitations, proposed timings, utility/fault-duty hold points, and outstanding questions.

| Customer Representative Name: | ________________________________ |
| --- | --- |
| Title / Company: | ________________________________ |
| Signature: | ________________________________ |
| Date: | ________________________________ |